##### DRAFT EAST AFRICAN STANDARD

Industrial Diesel Oil (IDO) — Specification

EAST AFRICAN COMMUNITY

Copyright notice

This EAC document is copyright-protected by EAC. While the reproduction of this document by participants in the EAC standards development process is permitted without prior permission from EAC, neither this document nor any extract from it may be reproduced, stored or transmitted in any form for any other purpose without prior written permission from EAC.

Requests for permission to reproduce this document for the purpose of selling it should be addressed as shown below or to EAC’s member body in the country of the requester:

© East African Community 2023 — All rights reserved

East African Community

P.O. Box 1096,

Arusha

Tanzania

Tel: + 255 27 2162100

Fax: + 255 27 2162190

E-mail: eac@eachq.org

Web: www.eac-quality.net

Reproduction for sales purposes may be subject to royalty payments or a licensing agreement. Violators may be prosecuted.

Foreword

Development of the East African Standards has been necessitated by the need for harmonizing requirements governing quality of products and services in the East African Community. It is envisaged that through harmonized standardization, trade barriers that are encountered when goods and services are exchanged within the Community will be removed.

The Community has established an East African Standards Committee (EASC) mandated to develop and issue East African Standards (EAS). The Committee is composed of representatives of the National Standards Bodies in Partner States, together with the representatives from the public and private sector organizations in the community.

East African Standards are developed through Technical Committees that are representative of key stakeholders including government, academia, consumer groups, private sector and other interested parties. Draft East African Standards are circulated to stakeholders through the National Standards Bodies in the Partner States. The comments received are discussed and incorporated before finalization of standards, in accordance with the Principles and procedures for development of East African Standards.

East African Standards are subject to review, to keep pace with technological advances. Users of the East African Standards are therefore expected to ensure that they always have the latest versions of the standards they are implementing.

The committee responsible for this document is Technical Committee EASC/TC 068, Petroleum and petroleum products.

Attention is drawn to the possibility that some of the elements of this document may be subject of patent rights. EAC shall not be held responsible for identifying any or all such patent rights.

# Industrial diesel oil (IDO) — Specification1	Scope

This Draft East Africa Standard specifies requirements, sampling and test methods for Industrial Diesel Oil (IDO) used as a fuel for industrial applications such as heating, power generation and industrial furnaces.

# 2	Normative references

The following referenced documents referred to in the text in such a way that some or all of their content constitutes requirements of this document. For dated references, only the edition cited applies. For undated references, the latest edition of the referenced document (including any amendments) applies.

ASTM D93, Standard test methods for flash point by Pensky-Martens closed cup tester

ASTM D95, Standard test method for water in petroleum products and bituminous materials by distillation

ASTM D97, Standard test method for pour point of petroleum products

ASTM D189, Standard test method for Conradson carbon residue of petroleum products

ASTM D240, Standard test method for heat of combustion of liquid hydrocarbon fuels by bomb calorimeter

ASTM D445, Standard test method for kinematic viscosity of transparent and opaque liquids (and calculation of dynamic viscosity)

ASTM D473, Standard test method for sediment in crude oils and fuel oils by the extraction method

ASTM D482, Standard test method for ash from petroleum products

ASTM D974, Standard test method for acid and base number by color-indicator titration

ASTM D1298, Standard test method for density, relative density, or API gravity of crude petroleum and liquid petroleum products by hydrometer method

ASTM D1552, Standard test method for sulfur in petroleum products by high temperature combustion and infrared (IR) detection or Thermal Conductivity Detection (TCD)

ASTM D2622, Standard test method for sulfur in petroleum products by wavelength dispersive X-ray fluorescence spectrometry

ASTM D3228, Standard test method for total nitrogen in lubricating oils and fuel oils by modified Kjeldahl method

ASTM D4057, Standard practice for manual sampling of petroleum and petroleum products

ASTM D4177, Standard practice for automatic sampling of petroleum and petroleum products

ASTM D4294, Standard test method for sulfur in petroleum and petroleum products by energy dispersive X-ray fluorescence spectrometry

ASTM D4530, Standard test method for determination of carbon residue (micro method)

ASTM D4868, Standard test method for estimation of net and gross heat of combustion of hydrocarbon burner and diesel fuels

ASTM D5184, Standard test methods for determination of Aluminum and Silicon in fuel oils by ashing, fusion, inductively coupled plasma atomic emission spectrometry, and atomic absorption spectrometry

ASTM D5623, Standard test method for sulfur compounds in light petroleum liquids by gas chromatography and sulfur selective detection

ASTM D5708, Standard test methods for determination of Nickel, Vanadium, and Iron in crude oils and residual fuels by Inductively Coupled Plasma (ICP) atomic emission spectrometry

ASTM D5863, Standard test methods for determination of Nickel, Vanadium, Iron, and Sodium in crude oils and residual fuels by flame atomic absorption spectrometry

ASTM D5950, Standard test method for pour point of petroleum products (automatic tilt method)

ASTM D6560, Standard test method for determination of asphaltenes (heptane insolubles) in crude petroleum and petroleum products

ASTM D6892, Standard test method for pour point of petroleum products (robotic tilt method)

IP 4, Petroleum products — Determination of ash

IP 34, Determination of flash point — Pensky-Martens closed cup method

IP 53, Crude petroleum and fuel oils — Determination of sediment ― Extraction method

IP 71: Section 1: Petroleum products — Transparent and opaque liquids — Determination of kinematic viscosity and calculation of dynamic viscosity

IP 143, Determination of asphaltenes (heptane insolubles) in crude petroleum and petroleum products

IP 336, Petroleum products ― Determination of sulfur content ― Energy-dispersive-X-ray fluorescence method

IP 365, Crude petroleum and petroleum products — Determination of density — Oscillating U-tube method

IP 375, Petroleum products — Total sediment in residual fuel oils — Part 1: Determination by hot filtration

IP 390, Petroleum products — Total sediment in residual fuel oils — Part 2: Determination using standard procedures for ageing

IP 398, Petroleum products — Determination of carbon residue — Micro method

IP 470, Determination of Aluminium, Silicon, Vanadium, Nickel, Iron, Calcium, Zinc and Sodium in residual fuel oil by ashing, fusion and atomic absorption spectrometry

IP 500, Determination of the phosphorus content of residual fuels by ultra-violet spectrometry

IP 501, Determination of Aluminium, Silicon, Vanadium, Nickel, Iron, Sodium, Calcium, Zinc and Phosphorous in residual fuel oil by ashing, fusion and inductively coupled plasma emission spectrometry

ISO 2719, Determination of flash point — Pensky-Martens closed cup method — Amendment 1: Thermometers correction

ISO 3016, Petroleum and related products from natural or synthetic sources — Determination of pour point

ISO 3104, Petroleum products — Transparent and opaque liquids — Determination of kinematic viscosity and calculation of dynamic viscosity

ISO 3733, Petroleum products and bituminous materials — Determination of water — Distillation method

ISO 3735, Crude petroleum and fuel oils — Determination of sediment — Extraction method

ISO 6245, Petroleum products — Determination of ash

ISO 6615, Petroleum products — Determination of carbon residue — Conradson method

ISO 8217, Petroleum products — Fuels (class F) — Specifications of marine fuels

ISO 8754, Petroleum products — Determination of sulfur content — Energy-dispersive X-ray fluorescence spectrometry

ISO 10370, Petroleum products — Determination of carbon residue — Micro method

ISO 10478, Petroleum products — Determination of aluminium and silicon in fuel oils — Inductively coupled plasma emission and atomic absorption spectroscopy methods

ISO 12185, Crude petroleum and petroleum products — Determination of density — Oscillating U-tube method

# 3	Terms and definitions

For the purposes of this document, the following terms and definitions apply.

ISO and IEC maintain terminological databases for use in standardization at the following addresses:

—	ISO Online browsing platform: available at http://www.iso.org/obp

3.1 additive

material added to industrial diesel oil usually in small amounts, to impart or enhance desirable properties or to suppress undesirable properties

3.2

Industrial Diesel Oil (IDO)

is a fuel mainly used for heating, steam and power generation in industrial and hospitality applications.

# 4	Requirements

## 4.1	General requirements

4.1.1	 Industrial diesel oil shall be a homogeneous blend of hydrocarbons derived from petroleum refining. Small amounts of additives may be added to improve some aspects of the Industrial diesel oil characteristics and performance.

4.1.2	industrial diesel oils shall be clear and bright, free from inorganic acids, foreign matter or any other contaminant.

4.1.3when stored in normal conditions industrial diesel oils shall remain uniform and show no separation.

## 4.1.4	4.2	Specific requirements

4.2.1	 Industrial diesel oils shall comply with the requirements given in Table 1, when tested in accordance with the test methods specified therein.

4.2.2	Alternative methods for testing respective parameters given in Table 1 are listed in Annex A. However, in case of dispute, the test methods given in Table 1 shall be the reference test methods.Table 1 — Specific requirements for industrial diesel oils

| S/N | Property | Requirement | Test method |
| --- | --- | --- | --- |
| i | Kinematic viscosity at 40 ºC, cSt, max. | 11 | ASTM D445 |
| ii | Density at 20 ºC, kg/l, max. | 0.920 | ASTM D1298 ASTM D 4052 |
| iii | Carbon residue Conradson, 100% residue, %(m/m) | 0.45 | ASTM D189 IP 13 |
| iv | Sulphur content, % wt., max. | 1.5 | ASTM D4294 |
| v | Vanadium content, mg/kg, max. | 100 | IP 501 |
| vi | Asphaltenes, % wt., max. | 0.3 | IP 143 |
| vii | Ash content, % wt., max. | 0.02 | ASTM D482 |
| viii | Sodium content, mg/kg, max. | 1/3 vanadium | IP 501 |
| ix | Water content, % vol, max. | 0.25 | ASTM D95 |
| x | Pour point, ºC, max. | 10 | ASTM D97 |
| xi | Flash point, ºC, min. | 66 | ASTM D93 |
| xii | Diesel index, min | 51 | ASTM D 287 ASTM D 611 |
| xiii | Net calorific value, MJ/kg, min. | 44.8 | ASTM D4868 |
| xv | Nitrogen content, % wt., max. | 0.4 | ASTM D3228 |
| xvi | Sediment by extraction, % wt., max. | 0.02 | ASTM D473 |
| xix | Neutralization strong acid number, mg KOH/g Total acid number, mg/KOH/g, max | Nil 0.5 | ASTM D974 ASTM D 664 |
| xx | Calcium, mg/kg, max. | 30 | IP 470 |
| xxi | Phosphorus, mg/kg, max. | 15 | IP 500 |
| xxii | Zinc, mg/kg, max. | 15 | IP 470 |

# 5	Packaging

The condition of the containers, rail tankers and road tank vehicles shall be such as not to be detrimental to the quality of the fuel during transportation and storage. The containers shall be acceptably sealed or leak proof, clean and free from materials soluble in industrial diesel oil as applicable.

# 6	Labelling

6.1	The following information shall be indelibly and legibly marked on the container, or on a label affixed to the container:

- manufacturer’s/supplier’s name and physical address;

- name of product as “industrial diesel oil”;

- net content;

- batch/lot number;

- words “FLAMMABLE MATERIAL”;

- warning “DANGER FUEL OIL”; and

- country of origin.

6.2	For bulk transportation, the above information shall be in the documentation accompanying the product.

# 7	Sampling

Sampling shall be done in accordance with ASTM D4057 or ASTM D4177.

Bibliography

[1]	KS 1309:1996, Specification for diesel fuels -Part 2.  Industrial diesel oil (IDO)